Material: Polyolefin
Shrink temperature: Start at 100℃, and shrink totally at 130℃
Voltage Rating: 3 Voltage Grades (1kV, 10kV, 35kV)
Color: black, red, milk-white(only for oil-resistant terminations)

Application: 
Suitable for termination kits for PVC, XLPE, and PILE Cable.

Technical Data

| Property | Test Method | Standard Value |  |
| --- | --- | --- | --- |
|  |  | Insulation breakout | Oil resistant breakout |
| Operating temperature | IEC 216 | -55℃～100℃ | -20℃～100℃ |
| Tensile strength | ASTM-D-2671 | ≥13MPa | ≥12MPa |
| Elongation | ASTM-D-2671 | ≥300% | ≥300% |
| Tensile strength after thermal aging | ASTM-D-2671 | ≥11MPa | ≥10MPa |
|  | 120℃/168hrs |  |  |
| Elongation after thermal aging | ASTM-D-2671 | ≥230% | ≥230% |
|  | 120℃/168hrs |  |  |
| Water absorption | ISO 62 | ≤0. 1% | ≤0. 1% |
| Volume resistance | IEC 93 | ≥1×1014Ω. cm | ≥1×1014Ω. cm |
| Oil resistance | ASTM-D-2671 | -- | ≥10MPa |
| Tensile strength after dipping | 70#cable oil/168hrs | -- | ≥10MPa |
| Oil resistance | ASTM-D-2671 | -- | 230% |
| Elongation at break after dipping | 70#cable oil/168hrs | -- | 230% |
| Dielectric strength | IEC 243 | ≥20kV/mm | ≥20kV/mm |

Specifications

| Part NO. |  | Breakout main diameter |  | Finger diameter |  | Full lemgth (mm) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | As supplied(mm) | After recovery(mm) | As supplied(mm) | After recovery(mm) |  |
| 2 cores breakout | HSCB2-24/12-#0 | ≥24 | ≤12 | ≤13 | ≤6 | 130±5 |
|  | HSCB2-38/20-#1 | ≥38 | ≤20 | ≤17 | ≤8 | 145±5 |
|  | HSCB2-48/25-#2 | ≥48 | ≤25 | ≤21 | ≤10 | 145±5 |
|  | HSCB2-60/35-#3 | ≥60 | ≤35 | ≤25 | ≤12 | 135±5 |
|  | HSCB2-72/40-#4 | ≥72 | ≤40 | ≤25 | ≤12 | 140±5 |
| 3 cores breakout | HSCB3-24/11-#-2 | ≥24 | ≤11 | ≤17 | ≤6 | 140±5 |
|  | HSCB3-48/18-#-1 | ≥48 | ≤18 | ≤22 | ≤8 | 170±5 |
|  | HSCB3-60/25-#0 | ≥60 | ≤25 | ≤28 | ≤9 | 175±5 |
|  | HSCB3-70/30-#1 | ≥70 | ≤30 | ≤36 | ≤14 | 215±5 |
|  | HSCB3-85/39-#2 | ≥85 | ≤39 | ≤45 | ≤16 | 225±5 |
|  | HSCB3-110/42-#3 | ≥110 | ≤42 | ≤53 | ≤19 | 245±5 |
|  | HSCB3-125/58-#4 | ≥125 | ≤58 | ≤63 | ≤25 | 245±5 |
|  | HSCB3-140/65-#5 | ≥140 | ≤65 | ≤63 | ≤25 | 245±5 |
| 4 cores breakout | HSCB4-38/10-#0 | ≥38 | ≤10 | ≤18 | ≤6 | 130±5 |
|  | HSCB4-50/16-#1 | ≥50 | ≤16 | ≤24 | ≤7 | 135±5 |
|  | HSCB4-70/23-#2 | ≥70 | ≤23 | ≤32 | ≤9 | 180±5 |
|  | HSCB4-80/30-#3 | ≥80 | ≤30 | ≤44 | ≤13 | 210±5 |
|  | HSCB4-90/35-#4 | ≥90 | ≤35 | ≤44 | ≤13 | 210±5 |
|  | HSCB4-110/40-#5 | ≥110 | ≤40 | ≤44 | ≤13 | 210±5 |
| 5 cores breakout | HSCB5-42/12-#0 | ≥42 | ≤12 | ≤21 | ≤5 | 155±5 |
|  | HSCB5-55/15-#1 | ≥55 | ≤15 | ≤29 | ≤7 | 170±5 |
|  | HSCB5-70/23-#2 | ≥70 | ≤23 | ≤38 | ≤10 | 170±5 |
|  | HSCB5-90/30-#3 | ≥90 | ≤30 | ≤51 | ≤13 | 180±5 |
|  | HSCB5-120/39-#4 | ≥120 | ≤39 | ≤47 | ≤14 | 205±5 |

Other sizes are available upon request.